## energy-storage-database
technology | type | carrier | parameter | year | value | unit | source | note | reference | ref_size_MW | EP_ratio_h
Lithium-Ion-LFP | electrochemical | lfp | investment | 2030 | 109.45 | $/kWh | Viswanathan_2022 | DC storage block | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | investment | 2030 | 27.57 | $/kWh | Viswanathan_2022 | DC storage BOS | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | investment | 2030 | 64.62 | $/kW | Viswanathan_2022 | Power Equipment | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | investment | 2030 | 5.78 | $/kW | Viswanathan_2022 | Controll and Communication | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | investment | 2030 | 35.19 | $/kWh | Viswanathan_2022 | System integration | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | investment | 2030 | 42.26 | $/kWh | Viswanathan_2022 | EPC | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | investment | 2030 | 50.71 | $/kWh | Viswanathan_2022 | Project Development | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | investment | 2030 | 21.05 | $/kW | Viswanathan_2022 | Grid integration | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | FOM | 2030 | 0.11855 | $/kWh-year | Viswanathan_2022 | 0.43 % of SB | p.28 (p.50) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | FOM | 2030 | 1.9386 | $/kW-year | Viswanathan_2022 | 30% assumed of power components every 10 years | p.28 (p.50) | 10 | 24
Lithium-Ion-LFP | electrochemical |  | decommissioning | 2030 | 0 | $/kWh | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | efficiency | 2030 | 0.91935 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.8452^0.5 | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | lifetime | 2030 | 16 | years | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | lifetime | 2030 | 16 | years | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | investment | 2021 | 167.25 | $/kWh | Viswanathan_2022 | DC storage block | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | investment | 2021 | 36.92 | $/kWh | Viswanathan_2022 | DC storage BOS | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | investment | 2021 | 73.05 | $/kW | Viswanathan_2022 | Power Equipment | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | investment | 2021 | 7.75 | $/kW | Viswanathan_2022 | Controll and Communication | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | investment | 2021 | 41.48 | $/kWh | Viswanathan_2022 | System integration | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | investment | 2021 | 49.8 | $/kWh | Viswanathan_2022 | EPC | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | investment | 2021 | 59.76 | $/kWh | Viswanathan_2022 | Project Development | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | investment | 2021 | 24.81 | $/kW | Viswanathan_2022 | Grid integration | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | FOM | 2021 | 0.15876 | $/kWh-year | Viswanathan_2022 | 0.43 % of SB | p.28 (p.50) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | FOM | 2021 | 2.1915 | $/kW-year | Viswanathan_2022 | 30% assumed of power components every 10 years | p.28 (p.50) | 10 | 24
Lithium-Ion-LFP | electrochemical |  | decommissioning | 2021 | 2.65 | $/kWh | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | efficiency | 2021 | 0.90879 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.8259^0.5 | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | elec-lfp-elec | lifetime | 2021 | 16 | years | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-LFP | electrochemical | lfp | lifetime | 2021 | 16 | years | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | investment | 2030 | 129.37 | $/kWh | Viswanathan_2022 | DC storage block | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | investment | 2030 | 26.68 | $/kWh | Viswanathan_2022 | DC storage BOS | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | investment | 2030 | 64.62 | $/kW | Viswanathan_2022 | Power Equipment | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | investment | 2030 | 5.78 | $/kW | Viswanathan_2022 | Controll and Communication | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | investment | 2030 | 40.16 | $/kWh | Viswanathan_2022 | System integration | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | investment | 2030 | 48.22 | $/kWh | Viswanathan_2022 | EPC | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | investment | 2030 | 57.86 | $/kWh | Viswanathan_2022 | Project Development | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | investment | 2030 | 21.05 | $/kW | Viswanathan_2022 | Grid integration | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | FOM | 2030 | 0.11472 | $/kWh-year | Viswanathan_2022 | 0.43 % of SB | p.28 (p.50) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | FOM | 2030 | 1.9386 | $/kW-year | Viswanathan_2022 | 30% assumed of power components every 10 years | p.28 (p.50) | 10 | 24
Lithium-Ion-NMC | electrochemical |  | decommissioning | 2030 | 0 | $/kWh | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | efficiency | 2030 | 0.91935 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.8452^0.5 | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | lifetime | 2030 | 13 | years | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | lifetime | 2030 | 13 | years | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | investment | 2021 | 197.7 | $/kWh | Viswanathan_2022 | DC storage block | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | investment | 2021 | 35.73 | $/kWh | Viswanathan_2022 | DC storage BOS | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | investment | 2021 | 73.05 | $/kW | Viswanathan_2022 | Power Equipment | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | investment | 2021 | 7.75 | $/kW | Viswanathan_2022 | Controll and Communication | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | investment | 2021 | 47.33 | $/kWh | Viswanathan_2022 | System integration | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | investment | 2021 | 56.82 | $/kWh | Viswanathan_2022 | EPC | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | investment | 2021 | 68.19 | $/kWh | Viswanathan_2022 | Project Development | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | investment | 2021 | 24.81 | $/kW | Viswanathan_2022 | Grid integration | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | FOM | 2021 | 0.15364 | $/kWh-year | Viswanathan_2022 | 0.43 % of SB | p.28 (p.50) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | FOM | 2021 | 2.1915 | $/kW-year | Viswanathan_2022 | 30% assumed of power components every 10 years | p.28 (p.50) | 10 | 24
Lithium-Ion-NMC | electrochemical |  | decommissioning | 2021 | 2.65 | $/kWh | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | efficiency | 2021 | 0.90879 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.8259^0.5 | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | elec-nmc-elec | lifetime | 2021 | 16 | years | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lithium-Ion-NMC | electrochemical | nmc | lifetime | 2021 | 16 | years | Viswanathan_2022 |  | p.24 (p.46) | 10 | 24
Lead-Acid | electrochemical | lead | investment | 2030 | 212.58 | $/kWh | Viswanathan_2022 | DC storage block | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | investment | 2030 | 33.75 | $/kWh | Viswanathan_2022 | DC storage BOS | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | investment | 2030 | 117.65 | $/kW | Viswanathan_2022 | Power Equipment | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | investment | 2030 | 5.79 | $/kW | Viswanathan_2022 | Controll and Communication | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | investment | 2030 | 32.36 | $/kWh | Viswanathan_2022 | System integration | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | investment | 2030 | 35.42 | $/kWh | Viswanathan_2022 | EPC | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | investment | 2030 | 45.43 | $/kWh | Viswanathan_2022 | Project Development | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | investment | 2030 | 21.05 | $/kW | Viswanathan_2022 | Grid integration | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | FOM | 2030 | 0.91409 | $/kWh-year | Viswanathan_2022 | 0.43 % of SB | p.28 (p.50) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | FOM | 2030 | 3.5295 | $/kW-year | Viswanathan_2022 | 30% assumed of power components every 10 years | p.28 (p.50) | 10 | 24
Lead-Acid | electrochemical |  | decommissioning | 2030 | 12.04 | $/kWh | Viswanathan_2022 |  | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | efficiency | 2030 | 0.88318 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.78^0.5 | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | lifetime | 2030 | 12 | years | Viswanathan_2022 |  | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | lifetime | 2030 | 12 | years | Viswanathan_2022 |  | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | investment | 2021 | 225.98 | $/kWh | Viswanathan_2022 | DC storage block | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | investment | 2021 | 45.2 | $/kWh | Viswanathan_2022 | DC storage BOS | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | investment | 2021 | 133 | $/kW | Viswanathan_2022 | Power Equipment | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | investment | 2021 | 7.75 | $/kW | Viswanathan_2022 | Controll and Communication | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | investment | 2021 | 38.14 | $/kWh | Viswanathan_2022 | System integration | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | investment | 2021 | 41.75 | $/kWh | Viswanathan_2022 | EPC | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | investment | 2021 | 53.54 | $/kWh | Viswanathan_2022 | Project Development | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | investment | 2021 | 24.81 | $/kW | Viswanathan_2022 | Grid integration | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | FOM | 2021 | 0.97171 | $/kWh-year | Viswanathan_2022 | 0.43 % of SB | p.28 (p.50) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | FOM | 2021 | 3.99 | $/kW-year | Viswanathan_2022 | 30% assumed of power components every 10 years | p.28 (p.50) | 10 | 24
Lead-Acid | electrochemical |  | decommissioning | 2021 | 16.89 | $/kWh | Viswanathan_2022 |  | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | efficiency | 2021 | 0.88318 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.78^0.5 | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | elec-lead-elec | lifetime | 2021 | 12 | years | Viswanathan_2022 |  | p.33 (p.55) | 10 | 24
Lead-Acid | electrochemical | lead | lifetime | 2021 | 12 | years | Viswanathan_2022 |  | p.33 (p.55) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | investment | 2030 | 157.79 | $/kWh | Viswanathan_2022 | DC storage block | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | investment | 2030 | 28.35 | $/kWh | Viswanathan_2022 | DC storage BOS | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | investment | 2030 | 117.65 | $/kW | Viswanathan_2022 | Power Equipment | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | investment | 2030 | 5.82 | $/kW | Viswanathan_2022 | Controll and Communication | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | investment | 2030 | 29.72 | $/kWh | Viswanathan_2022 | System integration | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | investment | 2030 | 34.2 | $/kWh | Viswanathan_2022 | EPC | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | investment | 2030 | 39.33 | $/kWh | Viswanathan_2022 | Project Development | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | investment | 2030 | 21.21 | $/kW | Viswanathan_2022 | Grid integration | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | FOM | 2030 | 0.6785 | $/kWh-year | Viswanathan_2022 | 0.43 % of SB | p.28 (p.50) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | FOM | 2030 | 3.5295 | $/kW-year | Viswanathan_2022 | 30% assumed of power components every 10 years | p.28 (p.50) | 10 | 24
Vanadium-Redox-Flow | electrochemical |  | decommissioning | 2030 | 19.77 | $/kWh | Viswanathan_2022 |  | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | efficiency | 2030 | 0.80623 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.65^0.5 | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | lifetime | 2030 | 12 | years | Viswanathan_2022 |  | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | lifetime | 2030 | 12 | years | Viswanathan_2022 |  | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | investment | 2021 | 189.83 | $/kWh | Viswanathan_2022 | DC storage block | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | investment | 2021 | 37.97 | $/kWh | Viswanathan_2022 | DC storage BOS | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | investment | 2021 | 133 | $/kW | Viswanathan_2022 | Power Equipment | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | investment | 2021 | 7.8 | $/kW | Viswanathan_2022 | Controll and Communication | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | investment | 2021 | 35.03 | $/kWh | Viswanathan_2022 | System integration | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | investment | 2021 | 40.3 | $/kWh | Viswanathan_2022 | EPC | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | investment | 2021 | 46.35 | $/kWh | Viswanathan_2022 | Project Development | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | investment | 2021 | 25 | $/kW | Viswanathan_2022 | Grid integration | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | FOM | 2021 | 0.81627 | $/kWh-year | Viswanathan_2022 | 0.43 % of SB | p.28 (p.50) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | FOM | 2021 | 3.99 | $/kW-year | Viswanathan_2022 | 30% assumed of power components every 10 years | p.28 (p.50) | 10 | 24
Vanadium-Redox-Flow | electrochemical |  | decommissioning | 2021 | 22.95 | $/kWh | Viswanathan_2022 |  | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | efficiency | 2021 | 0.80623 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.65^0.5 | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | elec-vanadium-elec | lifetime | 2021 | 12 | years | Viswanathan_2022 |  | p.42 (p.64) | 10 | 24
Vanadium-Redox-Flow | electrochemical | vanadium | lifetime | 2021 | 12 | years | Viswanathan_2022 |  | p.42 (p.64) | 10 | 24
Ni-Zn | electrochemical | nizn | investment | 2030 | 158 | $/kWh | Viswanathan_2022 | DC storage block | p.59 (p.81) Table 4.14 | 10 | 24
Ni-Zn | electrochemical | nizn | investment | 2030 | 27 | $/kWh | Viswanathan_2022 | DC storage BOS | p.59 (p.81) Table 4.16 | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | investment | 2030 | 64.62 | $/kW | Viswanathan_2022 | Power Equipment | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | investment | 2030 | 5.78 | $/kW | Viswanathan_2022 | Controll and Communication | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | nizn | investment | 2030 | 31.67 | $/kWh | Viswanathan_2022 | System integration | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | nizn | investment | 2030 | 38.03 | $/kWh | Viswanathan_2022 | EPC | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | nizn | investment | 2030 | 45.64 | $/kWh | Viswanathan_2022 | Project Development | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | investment | 2030 | 21.05 | $/kW | Viswanathan_2022 | Grid integration | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | nizn | FOM | 2030 | 0.6794 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | FOM | 2030 | 1.9386 | $/kW-year | Viswanathan_2022 | Guesstimate 30% assumed of power components every 10 years | p.51-52 in section 4.4.2 | 10 | 24
Ni-Zn | electrochemical |  | decommissioning | 2030 | 0 | $/kWh | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | efficiency | 2030 | 0.9 |  | Viswanathan_2022 | ((0.75-0.87)/2)^0.5 mean value of range efficiency is not RTE but single way AC-store conversion | p.59 (p.81) | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | lifetime | 2030 | 15 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Ni-Zn | electrochemical | nizn | lifetime | 2030 | 15 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Ni-Zn | electrochemical | nizn | investment | 2021 | 197 | $/kWh | Viswanathan_2022 | DC storage block | p.59 (p.81) Table 4.13 | 10 | 24
Ni-Zn | electrochemical | nizn | investment | 2021 | 30 | $/kWh | Viswanathan_2022 | DC storage BOS | p.59 (p.81) Table 4.15 | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | investment | 2021 | 73.05 | $/kW | Viswanathan_2022 | Power Equipment | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | investment | 2021 | 7.75 | $/kW | Viswanathan_2022 | Controll and Communication | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | nizn | investment | 2021 | 41.48 | $/kWh | Viswanathan_2022 | System integration | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | nizn | investment | 2021 | 49.8 | $/kWh | Viswanathan_2022 | EPC | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | nizn | investment | 2021 | 59.76 | $/kWh | Viswanathan_2022 | Project Development | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | investment | 2021 | 24.81 | $/kW | Viswanathan_2022 | Grid integration | p.59 (p.81) same as Li-LFP | 10 | 24
Ni-Zn | electrochemical | nizn | FOM | 2021 | 0.8471 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | FOM | 2021 | 2.1915 | $/kW-year | Viswanathan_2022 | Guesstimate 30% assumed of power components every 10 years | p.51-52 in section 4.4.2 | 10 | 24
Ni-Zn | electrochemical |  | decommissioning | 2021 | 0 | $/kWh | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | efficiency | 2021 | 0.89163 |  | Viswanathan_2022 | ((0.71-0.88)/2)^0.5 mean value of range efficiency is not RTE but single way AC-store conversion | p.59 (p.81) | 10 | 24
Ni-Zn | electrochemical | elec-nizn-elec | lifetime | 2021 | 15 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Ni-Zn | electrochemical | nizn | lifetime | 2021 | 15 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | investment | 2030 | 277 | $/kWh | Viswanathan_2022 | DC storage block | p.59 (p.81) Table 4.14 | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | investment | 2030 | 70 | $/kWh | Viswanathan_2022 | DC storage BOS | p.59 (p.81) Table 4.16 | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | investment | 2030 | 64.62 | $/kW | Viswanathan_2022 | Power Equipment | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | investment | 2030 | 5.78 | $/kW | Viswanathan_2022 | Controll and Communication | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | investment | 2030 | 31.67 | $/kWh | Viswanathan_2022 | System integration | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | investment | 2030 | 38.03 | $/kWh | Viswanathan_2022 | EPC | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | investment | 2030 | 45.64 | $/kWh | Viswanathan_2022 | Project Development | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | investment | 2030 | 21.05 | $/kW | Viswanathan_2022 | Grid integration | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | FOM | 2030 | 1.1911 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | FOM | 2030 | 1.9386 | $/kW-year | Viswanathan_2022 | Guesstimate 30% assumed of power components every 10 years | p.51-52 in section 4.4.2 | 10 | 24
Zn-Br-Flow | electrochemical |  | decommissioning | 2030 | 0 | $/kWh | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | efficiency | 2030 | 0.83066 |  | Viswanathan_2022 | (0.69)^0.5 efficiency is not RTE but single way AC-store conversion | p.59 (p.81) Table 4.25 | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | lifetime | 2030 | 10 | years | Viswanathan_2022 |  | p.59 (p.81) Table 4.27 | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | lifetime | 2030 | 10 | years | Viswanathan_2022 |  | p.59 (p.81) Table 4.27 | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | investment | 2021 | 346 | $/kWh | Viswanathan_2022 | DC storage block | p.59 (p.81) Table 4.13 | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | investment | 2021 | 78 | $/kWh | Viswanathan_2022 | DC storage BOS | p.59 (p.81) Table 4.15 | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | investment | 2021 | 117.65 | $/kW | Viswanathan_2022 | Power Equipment | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | investment | 2021 | 5.82 | $/kW | Viswanathan_2022 | Controll and Communication | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | investment | 2021 | 29.72 | $/kWh | Viswanathan_2022 | System integration | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | investment | 2021 | 34.2 | $/kWh | Viswanathan_2022 | EPC | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | investment | 2021 | 39.33 | $/kWh | Viswanathan_2022 | Project Development | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | investment | 2021 | 21.21 | $/kW | Viswanathan_2022 | Grid integration | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | FOM | 2021 | 1.4878 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | FOM | 2021 | 3.5295 | $/kW-year | Viswanathan_2022 | Guesstimate 30% assumed of power components every 10 years | p.51-52 in section 4.4.2 | 10 | 24
Zn-Br-Flow | electrochemical |  | decommissioning | 2021 | 0 | $/kWh | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | efficiency | 2021 | 0.80623 |  | Viswanathan_2022 | (0.65)^0.5 efficiency is not RTE but single way AC-store conversion | p.59 (p.81) Table 4.25 | 10 | 24
Zn-Br-Flow | electrochemical | elec-znbrflow-elec | lifetime | 2021 | 10 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Br-Flow | electrochemical | znbrflow | lifetime | 2021 | 10 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | investment | 2030 | 140 | $/kWh | Viswanathan_2022 | DC storage block | p.59 (p.81) Table 4.14 | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | investment | 2030 | 25 | $/kWh | Viswanathan_2022 | DC storage BOS | p.59 (p.81) Table 4.16 | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | investment | 2030 | 117.65 | $/kW | Viswanathan_2022 | Power Equipment | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | investment | 2030 | 5.82 | $/kW | Viswanathan_2022 | Controll and Communication | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | investment | 2030 | 29.72 | $/kWh | Viswanathan_2022 | System integration | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | investment | 2030 | 34.2 | $/kWh | Viswanathan_2022 | EPC | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | investment | 2030 | 39.33 | $/kWh | Viswanathan_2022 | Project Development | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | investment | 2030 | 21.21 | $/kW | Viswanathan_2022 | Grid integration | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | FOM | 2030 | 0.602 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | FOM | 2030 | 3.5295 | $/kW-year | Viswanathan_2022 | Guesstimate 30% assumed of power components every 10 years | p.51-52 in section 4.4.2 | 10 | 24
Zn-Br-Nonflow | electrochemical |  | decommissioning | 2030 | 0 | $/kWh | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | efficiency | 2030 | 0.88882 |  | Viswanathan_2022 | (0.79)^0.5 efficiency is not RTE but single way AC-store conversion | p.59 (p.81) Table 4.25 | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | lifetime | 2030 | 15 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | lifetime | 2030 | 15 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | investment | 2021 | 175 | $/kWh | Viswanathan_2022 | DC storage block | p.59 (p.81) Table 4.13 | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | investment | 2021 | 28 | $/kWh | Viswanathan_2022 | DC storage BOS | p.59 (p.81) Table 4.15 | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | investment | 2021 | 117.65 | $/kW | Viswanathan_2022 | Power Equipment | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | investment | 2021 | 5.82 | $/kW | Viswanathan_2022 | Controll and Communication | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | investment | 2021 | 29.72 | $/kWh | Viswanathan_2022 | System integration | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | investment | 2021 | 34.2 | $/kWh | Viswanathan_2022 | EPC | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | investment | 2021 | 39.33 | $/kWh | Viswanathan_2022 | Project Development | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | investment | 2021 | 21.21 | $/kW | Viswanathan_2022 | Grid integration | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | FOM | 2021 | 0.7525 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | FOM | 2021 | 3.5295 | $/kW-year | Viswanathan_2022 | Guesstimate 30% assumed of power components every 10 years | p.51-52 in section 4.4.2 | 10 | 24
Zn-Br-Nonflow | electrochemical |  | decommissioning | 2021 | 0 | $/kWh | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | efficiency | 2021 | 0.86603 |  | Viswanathan_2022 | (0.75)^0.5 efficiency is not RTE but single way AC-store conversion | p.59 (p.81) Table 4.25 | 10 | 24
Zn-Br-Nonflow | electrochemical | elec-znbr-elec | lifetime | 2021 | 15 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Br-Nonflow | electrochemical | znbr | lifetime | 2021 | 15 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | investment | 2030 | 75.2 | $/kWh | Viswanathan_2022 | DC storage block | p.48 (p.70) text below Table 4.12 | 10 | 24
Zn-Air | electrochemical | znair | investment | 2030 | 17.1 | $/kWh | Viswanathan_2022 | DC storage BOS | p.48 (p.70) text below Table 4.12 | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | investment | 2030 | 117.65 | $/kW | Viswanathan_2022 | Power Equipment | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | investment | 2030 | 5.82 | $/kW | Viswanathan_2022 | Controll and Communication | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | investment | 2030 | 29.72 | $/kWh | Viswanathan_2022 | System integration | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | investment | 2030 | 34.2 | $/kWh | Viswanathan_2022 | EPC | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | investment | 2030 | 39.33 | $/kWh | Viswanathan_2022 | Project Development | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | investment | 2030 | 21.21 | $/kW | Viswanathan_2022 | Grid integration | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | FOM | 2030 | 0.32336 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | FOM | 2030 | 3.5295 | $/kW-year | Viswanathan_2022 | Guesstimate 30% assumed of power components every 10 years | p.51-52 in section 4.4.2 | 10 | 24
Zn-Air | electrochemical |  | decommissioning | 2030 | 0 | $/kWh | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | efficiency | 2030 | 0.79373 |  | Viswanathan_2022 | (0.63)^0.5 efficiency is not RTE but single way AC-store conversion | p.59 (p.81) Table 4.25 | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | lifetime | 2030 | 25 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | lifetime | 2030 | 25 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | investment | 2021 | 94 | $/kWh | Viswanathan_2022 | DC storage block | p.59 (p.81) Table 4.12 | 10 | 24
Zn-Air | electrochemical | znair | investment | 2021 | 19 | $/kWh | Viswanathan_2022 | DC storage BOS | p.59 (p.81) Table 4.12 | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | investment | 2021 | 117.65 | $/kW | Viswanathan_2022 | Power Equipment | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | investment | 2021 | 5.82 | $/kW | Viswanathan_2022 | Controll and Communication | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | investment | 2021 | 29.72 | $/kWh | Viswanathan_2022 | System integration | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | investment | 2021 | 34.2 | $/kWh | Viswanathan_2022 | EPC | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | investment | 2021 | 39.33 | $/kWh | Viswanathan_2022 | Project Development | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | investment | 2021 | 21.21 | $/kW | Viswanathan_2022 | Grid integration | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | FOM | 2021 | 0.4042 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | FOM | 2021 | 3.5295 | $/kW-year | Viswanathan_2022 | Guesstimate 30% assumed of power components every 10 years | p.51-52 in section 4.4.2 | 10 | 24
Zn-Air | electrochemical |  | decommissioning | 2021 | 0 | $/kWh | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | efficiency | 2021 | 0.76811 |  | Viswanathan_2022 | (0.59)^0.5 efficiency is not RTE but single way AC-store conversion | p.59 (p.81) Table 4.25 | 10 | 24
Zn-Air | electrochemical | elec-znair-elec | lifetime | 2021 | 25 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Zn-Air | electrochemical | znair | lifetime | 2021 | 25 | years | Viswanathan_2022 |  | p.59 (p.81) | 10 | 24
Compressed-Air-Adiabatic | mechanical | pair | investment | 2030 | 6.11 | $/kWh | Viswanathan_2022 | Cavern Storage | p.64 (p.86) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | elec-pair-elec | investment | 2030 | 1061 | $/kW | Viswanathan_2022 | Turbine Compressor BOP EPC Management | p.59 (p.81) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | pair | FOM | 2030 | 0.026273 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB 4.5.2.1 Fixed O&M p.62 (p.84) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | elec-pair-elec | FOM | 2030 | 9.83 | $/kW-year | Viswanathan_2022 |  | p.64 (p.86) Figure 4.14 | 1000 | 24
Compressed-Air-Adiabatic | mechanical | elec-pair-elec | efficiency | 2030 | 0.72111 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.52^0.5 | p.59 (p.81) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | elec-pair-elec | lifetime | 2030 | 60 | years | Viswanathan_2022 |  | p.59 (p.81) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | pair | lifetime | 2030 | 60 | years | Viswanathan_2022 |  | p.59 (p.81) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | pair | investment | 2021 | 6.11 | $/kWh | Viswanathan_2022 | Cavern Storage | p.64 (p.86) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | elec-pair-elec | investment | 2021 | 1061 | $/kW | Viswanathan_2022 | Turbine Compressor BOP EPC Management | p.59 (p.81) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | pair | FOM | 2021 | 0.026273 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB 4.5.2.1 Fixed O&M p.62 (p.84) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | elec-pair-elec | FOM | 2021 | 9.83 | $/kW-year | Viswanathan_2022 |  | p.64 (p.86) Figure 4.14 | 1000 | 24
Compressed-Air-Adiabatic | mechanical | elec-pair-elec | efficiency | 2021 | 0.72111 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.52^0.5 | p.59 (p.81) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | elec-pair-elec | lifetime | 2021 | 60 | years | Viswanathan_2022 |  | p.59 (p.81) | 1000 | 24
Compressed-Air-Adiabatic | mechanical | pair | lifetime | 2021 | 60 | years | Viswanathan_2022 |  | p.59 (p.81) | 1000 | 24
Pumped-Storage-Hydro | mechanical | phs | investment | 2030 | 64 | $/kWh | Viswanathan_2022 | Reservoir Construction & Infrastructure | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | investment | 2030 | 623 | $/kW | Viswanathan_2022 | Powerhouse Construction & Infrastructure | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | investment | 2030 | 392 | $/kW | Viswanathan_2022 | Electromechanical | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | investment | 2030 | 551.67 | $/kW | Viswanathan_2022 | Contigency Fee | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | phs | FOM | 2030 | 0.2752 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | FOM | 2030 | 15.59 | $/kW-year | Viswanathan_2022 |  | Figure 4.16 | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | efficiency | 2030 | 0.89443 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.8^0.5 | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | lifetime | 2030 | 60 | years | Viswanathan_2022 |  | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | phs | lifetime | 2030 | 60 | years | Viswanathan_2022 |  | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | phs | investment | 2021 | 64 | $/kWh | Viswanathan_2022 | Reservoir Construction & Infrastructure | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | investment | 2021 | 623 | $/kW | Viswanathan_2022 | Powerhouse Construction & Infrastructure | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | investment | 2021 | 392 | $/kW | Viswanathan_2022 | Electromechanical | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | investment | 2021 | 551.67 | $/kW | Viswanathan_2022 | Contigency Fee | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | phs | FOM | 2021 | 0.2752 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | FOM | 2021 | 15.59 | $/kW-year | Viswanathan_2022 |  | Figure 4.16 | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | efficiency | 2021 | 0.89443 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.8^0.5 | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | elec-phs-elec | lifetime | 2021 | 60 | years | Viswanathan_2022 |  | p.68 (p.90) | 10 | 24
Pumped-Storage-Hydro | mechanical | phs | lifetime | 2021 | 60 | years | Viswanathan_2022 |  | p.68 (p.90) | 10 | 24
Gravity-Brick | mechanical | gravity | investment | 2030 | 148.75 | $/kWh | Viswanathan_2022 | Gravitational Capital (SB+BOS) | p.71 (p.94) text at the bottom speaks about 15% cost reduction for 2030 compared to 2021 | 1000 | 24
Gravity-Brick | mechanical | elec-gravity-elec | investment | 2030 | 466 | $/kW | Viswanathan_2022 | Power Equipment | p.71 (p.94) text at the bottom speaks about 0% cost reduction for 2030 compared to 2021 | 1000 | 24
Gravity-Brick | mechanical | gravity | investment | 2030 | 27.73 | $/kWh | Viswanathan_2022 | EPC Fee Project Development Grid integration | p.80 (p.102) Figure 4.18 | 1000 | 24
Gravity-Brick | mechanical | elec-gravity-elec | FOM | 2030 | 6.99 | $/kW-year | Viswanathan_2022 | 1.5 percent of capital cost | p.76 (p.98) Sentence 1 in 4.7.2 Operating Costs | 1000 | 24
Gravity-Brick | mechanical | elec-gravity-elec | efficiency | 2030 | 0.92736 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.86^0.5 | p.77 (p.99) Table 4.36 | 1000 | 24
Gravity-Brick | mechanical | elec-gravity-elec | lifetime | 2030 | 41.7 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.36 | 1000 | 24
Gravity-Brick | mechanical | gravity | lifetime | 2030 | 41.7 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.36 | 1000 | 24
Gravity-Brick | mechanical | gravity | investment | 2021 | 175 | $/kWh | Viswanathan_2022 | Gravitational Capital (SB+BOS) | p.75 (p.97) Table 4.32 | 1000 | 24
Gravity-Brick | mechanical | elec-gravity-elec | investment | 2021 | 466 | $/kW | Viswanathan_2022 | Power Equipment | p.74 (p.96) Table 4.31 | 1000 | 24
Gravity-Brick | mechanical | gravity | investment | 2021 | 31.7 | $/kWh | Viswanathan_2022 | EPC Fee Project Development Grid integration | p.80 (p.102) Figure 4.18 | 1000 | 24
Gravity-Brick | mechanical | elec-gravity-elec | FOM | 2021 | 6.99 | $/kW-year | Viswanathan_2022 | 1.5 percent of capital cost | p.76 (p.98) Sentence 1 in 4.7.2 Operating Costs | 1000 | 24
Gravity-Brick | mechanical | elec-gravity-elec | efficiency | 2021 | 0.92736 |  | Viswanathan_2022 | AC-AC efficiency at transformer level 0.86^0.5 | p.77 (p.99) Table 4.36 | 1000 | 24
Gravity-Brick | mechanical | elec-gravity-elec | lifetime | 2021 | 41.7 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.36 | 1000 | 24
Gravity-Brick | mechanical | gravity | lifetime | 2021 | 41.7 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.36 | 1000 | 24
Gravity-Water-Aboveground | mechanical | gravitywa | investment | 2030 | 108.8 | $/kWh | Viswanathan_2022 | Gravitational Capital (SB+BOS) | p.71 (p.94) text at the bottom speaks about 15% cost reduction for 2030 compared to 2021 | 1000 | 24
Gravity-Water-Aboveground | mechanical | elec-gravitywa-elec | investment | 2030 | 410 | $/kW | Viswanathan_2022 | Power Equipment | p.71 (p.94) text at the bottom speaks about 0% cost reduction for 2030 compared to 2021 | 1000 | 24
Gravity-Water-Aboveground | mechanical | gravitywa | investment | 2030 | 27.73 | $/kWh | Viswanathan_2022 | EPC Fee Project Development Grid integration | p.80 (p.102) Figure 4.18 | 1000 | 24
Gravity-Water-Aboveground | mechanical | elec-gravitywa-elec | FOM | 2030 | 6.15 | $/kW-year | Viswanathan_2022 | 1.5 percent of capital cost | p.76 (p.98) Sentence 1 in 4.7.2 Operating Costs | 1000 | 24
Gravity-Water-Aboveground | mechanical | elec-gravitywa-elec | efficiency | 2030 | 0.90139 |  | Viswanathan_2022 | AC-AC efficiency at transformer level ((0.785+0.84)/2)^0.5 | p.77 (p.99) Table 4.37 | 1000 | 24
Gravity-Water-Aboveground | mechanical | elec-gravitywa-elec | lifetime | 2030 | 60 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.37 | 1000 | 24
Gravity-Water-Aboveground | mechanical | gravitywa | lifetime | 2030 | 60 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.37 | 1000 | 24
Gravity-Water-Aboveground | mechanical | gravitywa | investment | 2021 | 128 | $/kWh | Viswanathan_2022 | Gravitational Capital (SB+BOS) | p.75 (p.97) Table 4.32 | 1000 | 24
Gravity-Water-Aboveground | mechanical | elec-gravitywa-elec | investment | 2021 | 410 | $/kW | Viswanathan_2022 | Power Equipment | p.74 (p.96) Table 4.31 | 1000 | 24
Gravity-Water-Aboveground | mechanical | gravitywa | investment | 2021 | 31.7 | $/kWh | Viswanathan_2022 | EPC Fee Project Development Grid integration | p.80 (p.102) Figure 4.18 | 1000 | 24
Gravity-Water-Aboveground | mechanical | elec-gravitywa-elec | FOM | 2021 | 6.15 | $/kW-year | Viswanathan_2022 | 1.5 percent of capital cost | p.76 (p.98) Sentence 1 in 4.7.2 Operating Costs | 1000 | 24
Gravity-Water-Aboveground | mechanical | elec-gravitywa-elec | efficiency | 2021 | 0.90139 |  | Viswanathan_2022 | AC-AC efficiency at transformer level ((0.785+0.84)/2)^0.5 | p.77 (p.99) Table 4.37 | 1000 | 24
Gravity-Water-Aboveground | mechanical | elec-gravitywa-elec | lifetime | 2021 | 60 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.37 | 1000 | 24
Gravity-Water-Aboveground | mechanical | gravitywa | lifetime | 2021 | 60 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.37 | 1000 | 24
Gravity-Water-Underground | mechanical | gravitywu | investment | 2030 | 79.9 | $/kWh | Viswanathan_2022 | Gravitational Capital (SB+BOS) | p.71 (p.94) text at the bottom speaks about 15% cost reduction for 2030 compared to 2021 | 1000 | 24
Gravity-Water-Underground | mechanical | elec-gravitywu-elec | investment | 2030 | 1015 | $/kW | Viswanathan_2022 | Power Equipment | p.71 (p.94) text at the bottom speaks about 0% cost reduction for 2030 compared to 2021 | 1000 | 24
Gravity-Water-Underground | mechanical | gravitywu | investment | 2030 | 27.73 | $/kWh | Viswanathan_2022 | EPC Fee Project Development Grid integration | p.80 (p.102) Figure 4.18 | 1000 | 24
Gravity-Water-Underground | mechanical | elec-gravitywu-elec | FOM | 2030 | 15.225 | $/kW-year | Viswanathan_2022 | 1.5 percent of capital cost | p.76 (p.98) Sentence 1 in 4.7.2 Operating Costs | 1000 | 24
Gravity-Water-Underground | mechanical | elec-gravitywu-elec | efficiency | 2030 | 0.90139 |  | Viswanathan_2022 | AC-AC efficiency at transformer level ((0.785+0.84)/2)^0.5 | p.77 (p.99) Table 4.37 | 1000 | 24
Gravity-Water-Underground | mechanical | elec-gravitywu-elec | lifetime | 2030 | 60 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.37 | 1000 | 24
Gravity-Water-Underground | mechanical | gravitywu | lifetime | 2030 | 60 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.37
Gravity-Water-Underground | mechanical | gravitywu | investment | 2021 | 94 | $/kWh | Viswanathan_2022 | Gravitational Capital (SB+BOS) | p.75 (p.97) Table 4.32 | 1000 | 24
Gravity-Water-Underground | mechanical | elec-gravitywu-elec | investment | 2021 | 1015 | $/kW | Viswanathan_2022 | Power Equipment | p.74 (p.96) Table 4.31 | 1000 | 24
Gravity-Water-Underground | mechanical | gravitywu | investment | 2021 | 31.7 | $/kWh | Viswanathan_2022 | EPC Fee Project Development Grid integration | p.80 (p.102) Figure 4.18 | 1000 | 24
Gravity-Water-Underground | mechanical | elec-gravitywu-elec | FOM | 2021 | 15.225 | $/kW-year | Viswanathan_2022 | 1.5 percent of capital cost | p.76 (p.98) Sentence 1 in 4.7.2 Operating Costs | 1000 | 24
Gravity-Water-Underground | mechanical | elec-gravitywu-elec | efficiency | 2021 | 0.90139 |  | Viswanathan_2022 | AC-AC efficiency at transformer level ((0.785+0.84)/2)^0.5 | p.77 (p.99) Table 4.37 | 1000 | 24
Gravity-Water-Underground | mechanical | elec-gravitywu-elec | lifetime | 2021 | 60 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.37 | 1000 | 24
Gravity-Water-Underground | mechanical | gravitywu | lifetime | 2021 | 60 | years | Viswanathan_2022 |  | p.77 (p.99) Table 4.37 | 1000 | 24
Hydrogen | electrochemical | h2cavern-elec | investment | 2030 | 425 | $/kW | Viswanathan_2022 | Fuel Cell | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical | elec-h2cavern | investment | 2030 | 350 | $/kW | Viswanathan_2022 | Electrolyzer | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical | h2cavern | investment | 2030 | 5.36 | $/kWh | Viswanathan_2022 | Cavern Storage | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical | h2cavern-elec | investment | 2030 | 39.3 | $/kW | Viswanathan_2022 | Compressor | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical |  | investment | 2030 | 39 | $/kW | Viswanathan_2022 | Inverter | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical |  | investment | 2030 | 84 | $/kW | Viswanathan_2022 | Rectifier | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical |  | investment | 2030 | 1.06 | $/kW | Viswanathan_2022 | Controll and Communication | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical |  | investment | 2030 | 16.3 | $/kW | Viswanathan_2022 | Grid integration | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical |  | FOM | 2030 | 0.023048 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB =(C38+C39)*0.43/4 | 10 | 24
Hydrogen | electrochemical | reference_value | FOM | 2030 | 4.9405 | $/kW-year | Viswanathan_2022 | derived | 30% assumed of power components every 10 years =(C45+C41+C40)*0.3+1.94 | 10 | 24
Hydrogen | electrochemical | elec-h2cavern | FOM | 2030 | 2.4703 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 10 | 24
Hydrogen | electrochemical | h2cavern-elec | FOM | 2030 | 2.4703 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 10 | 24
Hydrogen | electrochemical | h2cavern-elec | efficiency | 2030 | 0.69629 |  | Viswanathan_2022 | Electrolyzer | p.111 (p.133) include inverter 0.98 & transformer efficiency 0.98 | 10 | 24
Hydrogen | electrochemical | elec-h2cavern | efficiency | 2030 | 0.48692 |  | Viswanathan_2022 | Fuel Cell | p.111 (p.133) include inverter 0.98 & transformer efficiency 0.98 | 10 | 24
Hydrogen | electrochemical | h2cavern-elec | lifetime | 2030 | 30 | years | Viswanathan_2022 |  | p.111 (p.133) | 10 | 24
Hydrogen | electrochemical | elec-h2cavern | lifetime | 2030 | 30 | years | Viswanathan_2022 |  | p.111 (p.133) | 10 | 24
Hydrogen | electrochemical | h2cavern | lifetime | 2030 | 30 | years | Viswanathan_2022 |  | p.111 (p.133) | 10 | 24
Hydrogen | electrochemical | h2cavern-elec | investment | 2021 | 1320 | $/kW | Viswanathan_2022 | Fuel Cell | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical | elec-h2cavern | investment | 2021 | 1316 | $/kW | Viswanathan_2022 | Electrolyzer | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical | h2cavern | investment | 2021 | 5.36 | $/kWh | Viswanathan_2022 | Cavern Storage | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical | h2cavern-elec | investment | 2021 | 39.3 | $/kW | Viswanathan_2022 | Compressor | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical |  | investment | 2021 | 67 | $/kW | Viswanathan_2022 | Inverter | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical |  | investment | 2021 | 130 | $/kW | Viswanathan_2022 | Rectifier | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical |  | investment | 2021 | 1.5 | $/kW | Viswanathan_2022 | Controll and Communication | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical |  | investment | 2021 | 19.89 | $/kW | Viswanathan_2022 | Grid integration | p.113 (p.135) | 10 | 24
Hydrogen | electrochemical |  | FOM | 2021 | 0.023048 | $/kWh-year | Viswanathan_2022 | derived | 0.43 % of SB =(C38+C39)*0.43/4 | 10 | 24
Hydrogen | electrochemical |  | FOM | 2021 | 12.9428 | $/kW-year | Viswanathan_2022 | derived | 30% assumed of power components every 10 years =(C45+C41+C40)*0.3+1.94 | 10 | 24
Hydrogen | thermal | elec-phes | FOM | 2021 | 6.4714 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 10 | 24
Hydrogen | thermal | phes-elec | FOM | 2021 | 6.4714 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 10 | 24
Hydrogen | electrochemical | h2cavern-elec | efficiency | 2021 | 0.69629 |  | Viswanathan_2022 | Electrolyzer | p.111 (p.133) include inverter 0.98 & transformer efficiency 0.98 | 10 | 24
Hydrogen | electrochemical | elec-h2cavern | efficiency | 2021 | 0.48692 |  | Viswanathan_2022 | Fuel Cell | p.111 (p.133) include inverter 0.98 & transformer efficiency 0.98 | 10 | 24
Hydrogen | electrochemical | h2cavern-elec | lifetime | 2021 | 30 | years | Viswanathan_2022 |  | p.111 (p.133) | 10 | 24
Hydrogen | electrochemical | elec-h2cavern | lifetime | 2021 | 30 | years | Viswanathan_2022 |  | p.111 (p.133) | 10 | 24
Hydrogen | electrochemical | h2cavern | lifetime | 2021 | 30 | years | Viswanathan_2022 |  | p.111 (p.133) | 10 | 24
Pumped-Heat | thermal | phes | investment | 2030 | 4.6 | $/kWh | Viswanathan_2022 | Molten Salt based SB and BOS | p.92 (p.114) | 1000 | 100
Pumped-Heat | thermal | reference_value | investment | 2030 | 1454 | $/kW | Viswanathan_2022 | Power Equipment | p.92 (p.114) | 1000 | 100
Pumped-Heat | thermal | elec-phes | investment | 2030 | 854.225 | $/kW | Georgiou_2018 | Power Equipment Charge | Figure 9 of reference roughly 80% of capital cost are power related 47%/80% of costs are required for liquefaction (charging) | 1000 | 100
Pumped-Heat | thermal | phes-elec | investment | 2030 | 599.775 | $/kW | Georgiou_2018 | Power Equipment Discharge |  | 1000 | 100
Pumped-Heat | thermal |  | investment | 2030 | 5.36 | $/kWh | Viswanathan_2022 | EPC fee | p.92 (p.114) | 1000 | 100
Pumped-Heat | thermal |  | investment | 2030 | 0.996 | $/kWh | Viswanathan_2022 | Project Development | p.92 (p.114) | 1000 | 100
Pumped-Heat | thermal |  | investment | 2030 | 1.992 | $/kWh | Viswanathan_2022 | Grid integration | p.92 (p.114) | 1000 | 100
Pumped-Heat | thermal |  | FOM | 2030 | 0.01978 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p.103 (p.125) | 1000 | 100
Pumped-Heat | thermal |  | FOM | 2030 | 6.2522 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p.103 (p.125) | 1000 | 100
Pumped-Heat | thermal | elec-phes | FOM | 2030 | 3.1261 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 100
Pumped-Heat | thermal | phes-elec | FOM | 2030 | 3.1261 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 100
Pumped-Heat | thermal | elec-phes | efficiency | 2030 | 0.99 |  | Viswanathan_2022 | Charger |  | 1000 | 100
Pumped-Heat | thermal | phes-elec | efficiency | 2030 | 0.62626 |  | Viswanathan_2022 | RTE 0.62 assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 100
Pumped-Heat | thermal | elec-phes | lifetime | 2030 | 33 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Pumped-Heat | thermal | phes-elec | lifetime | 2030 | 33 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Pumped-Heat | thermal | phes | lifetime | 2030 | 33 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Pumped-Heat | thermal | phes | investment | 2021 | 5.4 | $/kWh | Viswanathan_2022 | Molten Salt based SB and BOS | p.92 (p.114) | 1000 | 100
Pumped-Heat | thermal | reference_value | investment | 2021 | 1532 | $/kW | Viswanathan_2022 | Power Equipment | p.92 (p.114) | 1000 | 100
Pumped-Heat | thermal | elec-phes | investment | 2021 | 900.05 | $/kW | Georgiou_2018 | Power Equipment Charge | Figure 9 of reference roughly 80% of capital cost are power related 47%/80% of costs are required for liquefaction (charging) | 1000 | 100
Pumped-Heat | thermal | phes-elec | investment | 2021 | 631.95 | $/kW | Georgiou_2018 | Power Equipment Discharge |  | 1000 | 100
Pumped-Heat | thermal |  | investment | 2021 | 19.89 | $/kWh | Viswanathan_2022 | EPC fee | p.92 (p.114) | 1000 | 100
Pumped-Heat | thermal |  | investment | 2021 | 2.529 | $/kWh | Viswanathan_2022 | Project Development | p.92 (p.114) | 1000 | 100
Pumped-Heat | thermal |  | investment | 2021 | 5.058 | $/kWh | Viswanathan_2022 | Grid integration | p.92 (p.114) | 1000 | 100
Pumped-Heat | thermal |  | FOM | 2021 | 0.02322 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p.103 (p.125) | 1000 | 100
Pumped-Heat | thermal | reference_value | FOM | 2021 | 6.5876 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p.103 (p.125) | 1000 | 100
Pumped-Heat | thermal | elec-phes | FOM | 2021 | 3.2938 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 100
Pumped-Heat | thermal | phes-elec | FOM | 2021 | 3.2938 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 100
Pumped-Heat | thermal | elec-phes | efficiency | 2021 | 0.99 |  | Viswanathan_2022 | charge |  | 1000 | 100
Pumped-Heat | thermal | phes-elec | efficiency | 2021 | 0.60606 |  | Viswanathan_2022 | RTE 0.6 assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 100
Pumped-Heat | thermal | elec-phes | lifetime | 2021 | 30 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Pumped-Heat | thermal | phes-elec | lifetime | 2021 | 30 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Pumped-Heat | thermal | phes | lifetime | 2021 | 30 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Liquid-Air | thermal | lair | investment | 2030 | 133 | $/kWh | Viswanathan_2022 | Liquid Air SB and BOS | p.98 (p.120) | 1000 | 100
Liquid-Air | thermal | reference_value | investment | 2030 | 908 | $/kW | Viswanathan_2022 | Power Equipment | p.98 (p.120) | 1000 | 100
Liquid-Air | thermal | elec-lair | investment | 2030 | 533.45 | $/kW | Georgiou_2018 | Power Equipment Charge | Figure 9 of reference roughly 80% of capital cost are power related 47%/80% of costs are required for liquefaction (charging) | 1000 | 100
Liquid-Air | thermal | lair-elec | investment | 2030 | 374.55 | $/kW | Georgiou_2018 | Power Equipment Discharge |  | 1000 | 100
Liquid-Air | thermal |  | investment | 2030 | 7 | $/kWh | Viswanathan_2022 | EPC fee | p.98 (p.120) | 1000 | 100
Liquid-Air | thermal |  | investment | 2030 | 27 | $/kWh | Viswanathan_2022 | Project Development | p.98 (p.120) | 1000 | 100
Liquid-Air | thermal |  | investment | 2030 | 11.3 | $/kWh | Viswanathan_2022 | Grid integration | p.98 (p.120) | 1000 | 100
Liquid-Air | thermal |  | FOM | 2030 | 0.5719 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 100
Liquid-Air | thermal | reference_value | FOM | 2030 | 3.9044 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 100
Liquid-Air | thermal | elec-lair | FOM | 2030 | 1.9522 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 100
Liquid-Air | thermal | lair-elec | FOM | 2030 | 1.9522 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 100
Liquid-Air | thermal | elec-lair | efficiency | 2030 | 0.99 |  | Viswanathan_2022 |  |  | 1000 | 100
Liquid-Air | thermal | lair-elec | efficiency | 2030 | 0.55051 |  | Viswanathan_2022 | RTE 0.545 assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 100
Liquid-Air | thermal | elec-lair | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Liquid-Air | thermal | lair-elec | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Liquid-Air | thermal | lair | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Liquid-Air | thermal | lair | investment | 2021 | 157 | $/kWh | Viswanathan_2022 | Liquid Air SB and BOS | p.98 (p.120) | 1000 | 100
Liquid-Air | thermal | reference_value | investment | 2021 | 956 | $/kW | Viswanathan_2022 | Power Equipment | p.98 (p.120) | 1000 | 100
Liquid-Air | thermal | elec-lair | investment | 2021 | 561.65 | $/kW | Georgiou_2018 | Power Equipment Charge | Figure 9 of reference roughly 80% of capital cost are power related 47%/80% of costs are required for liquefaction (charging) | 1000 | 100
Liquid-Air | thermal | lair-elec | investment | 2021 | 394.35 | $/kW | Georgiou_2018 | Power Equipment Discharge |  | 1000 | 100
Liquid-Air | thermal |  | investment | 2021 | 8 | $/kWh | Viswanathan_2022 | EPC fee | p.98 (p.120) | 1000 | 100
Liquid-Air | thermal |  | investment | 2021 | 30 | $/kWh | Viswanathan_2022 | Project Development | p.98 (p.120) | 1000 | 100
Liquid-Air | thermal |  | investment | 2021 | 11.3 | $/kWh | Viswanathan_2022 | Grid integration | p.98 (p.120) | 1000 | 100
Liquid-Air | thermal |  | FOM | 2021 | 0.6751 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 100
Liquid-Air | thermal | reference_value | FOM | 2021 | 4.1108 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 100
Liquid-Air | thermal | elec-lair | FOM | 2021 | 2.0554 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 100
Liquid-Air | thermal | lair-elec | FOM | 2021 | 2.0554 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 100
Liquid-Air | thermal | elec-lair | efficiency | 2021 | 0.99 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 100
Liquid-Air | thermal | lair-elec | efficiency | 2021 | 0.525 |  | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Liquid-Air | thermal | elec-lair | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Liquid-Air | thermal | lair-elec | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Liquid-Air | thermal | lair | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 100
Sand | thermal | sand | investment | 2030 | 5.78 | $/kWh | Viswanathan_2022 | SB and BOS 0.85 of 2021 value | p.100 (p.122) | 1000 | 24
Sand | thermal | reference_value | investment | 2030 | 808.45 | $/kW | Viswanathan_2022 | Power Equipment 0.95 of 2021 value | p.100 (p.122) | 1000 | 24
Sand | thermal | elec-sand | investment | 2030 | 161.69 | $/kW | Georgiou_2018 | Power Equipment Charge | Guesstimate that charge is 20% of capital costs of power components for sensible thermal storage
Sand | thermal | sand-elec | investment | 2030 | 646.76 | $/kW | Georgiou_2018 | Power Equipment Discharge | Guesstimate that charge is 80% of capital costs of power components for sensible thermal storage
Sand | thermal |  | investment | 2030 | 1.734 | $/kWh | Viswanathan_2022 | EPC fee Project Development Grid integration | p.98 (p.120) | 1000 | 24
Sand | thermal |  | FOM | 2030 | 0.024854 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
Sand | thermal | reference_value | FOM | 2030 | 3.4763 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
Sand | thermal | elec-sand | FOM | 2030 | 1.7382 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 24
Sand | thermal | sand-elec | FOM | 2030 | 1.7382 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 24
Sand | thermal | sand-elec | efficiency | 2030 | 0.52525 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
Sand | thermal | elec-sand | efficiency | 2030 | 0.99 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
Sand | thermal | sand-elec | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Sand | thermal | elec-sand | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Sand | thermal | sand | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Sand | thermal | sand | investment | 2021 | 6.8 | $/kWh | Viswanathan_2022 | SB and BOS | p.101 (p.123) | 1000 | 24
Sand | thermal | reference_value | investment | 2021 | 851 | $/kW | Viswanathan_2022 | Power Equipment | p.101 (p.123) | 1000 | 24
Sand | thermal | elec-sand | investment | 2021 | 170.2 | $/kW | Georgiou_2018 | Power Equipment Charge | Guesstimate that charge is 20% of capital costs of power components for sensible thermal storage
Sand | thermal | sand-elec | investment | 2021 | 680.8 | $/kW | Georgiou_2018 | Power Equipment Discharge | Guesstimate that charge is 80% of capital costs of power components for sensible thermal storage
Sand | thermal |  | investment | 2021 | 2.04 | $/kWh | Viswanathan_2022 | EPC fee Project Development Grid integration | p.101 (p.123) | 1000 | 24
Sand | thermal |  | FOM | 2021 | 0.02924 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p.100 (p.122) | 1000 | 24
Sand | thermal | reference_value | FOM | 2021 | 3.6593 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
Sand | thermal | elec-sand | FOM | 2021 | 1.8296 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 24
Sand | thermal | sand-elec | FOM | 2021 | 1.8296 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 24
Sand | thermal | sand-elec | efficiency | 2021 | 0.50505 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
Sand | thermal | elec-sand | efficiency | 2021 | 0.99 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
Sand | thermal | sand-elec | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Sand | thermal | elec-sand | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Sand | thermal | sand | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
HighT-Molten-Salt | thermal | salthight | investment | 2030 | 81.175 | $/kWh | Viswanathan_2022 | SB and BOS 0.85 of 2021 value | p.98 (p.120) | 1000 | 24
HighT-Molten-Salt | thermal | reference_value | investment | 2030 | 808.45 | $/kW | Viswanathan_2022 | Power Equipment 0.95 of 2021 value | p.98 (p.120) | 1000 | 24
HighT-Molten-Salt | thermal | elec-salthight | investment | 2030 | 161.69 | $/kW | Georgiou_2018 | Power Equipment Charge | Guesstimate that charge is 20% of capital costs of power components for sensible thermal storage
HighT-Molten-Salt | thermal | salthight-elec | investment | 2030 | 646.76 | $/kW | Georgiou_2018 | Power Equipment Discharge | Guesstimate that charge is 80% of capital costs of power components for sensible thermal storage
HighT-Molten-Salt | thermal |  | investment | 2030 | 24.3525 | $/kWh | Viswanathan_2022 | EPC fee Project Development Grid integration | p.98 (p.120) | 1000 | 24
HighT-Molten-Salt | thermal |  | FOM | 2030 | 0.34905 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
HighT-Molten-Salt | thermal | reference_value | FOM | 2030 | 3.4763 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
HighT-Molten-Salt | thermal | elec-salthight | FOM | 2030 | 1.7382 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 24
HighT-Molten-Salt | thermal | salthight-elec | FOM | 2030 | 1.7382 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 24
HighT-Molten-Salt | thermal | salthight-elec | efficiency | 2030 | 0.44444 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
HighT-Molten-Salt | thermal | elec-salthight | efficiency | 2030 | 0.99 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
HighT-Molten-Salt | thermal | salthight-elec | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
HighT-Molten-Salt | thermal | elec-salthight | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
HighT-Molten-Salt | thermal | salthight | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
HighT-Molten-Salt | thermal | salthight | investment | 2021 | 95.5 | $/kWh | Viswanathan_2022 | SB and BOS | p.101 (p.123) | 1000 | 24
HighT-Molten-Salt | thermal | reference_value | investment | 2021 | 1029 | $/kW | Viswanathan_2022 | Power Equipment | p.101 (p.123) | 1000 | 24
HighT-Molten-Salt | thermal | elec-salthight | investment | 2021 | 205.8 | $/kW | Georgiou_2018 | Power Equipment Charge | Guesstimate that charge is 20% of capital costs of power components for sensible thermal storage
HighT-Molten-Salt | thermal | salthight-elec | investment | 2021 | 823.2 | $/kW | Georgiou_2018 | Power Equipment Discharge | Guesstimate that charge is 80% of capital costs of power components for sensible thermal storage
HighT-Molten-Salt | thermal |  | investment | 2021 | 28.65 | $/kWh | Viswanathan_2022 | EPC fee Project Development Grid integration | p.101 (p.123) | 1000 | 24
HighT-Molten-Salt | thermal |  | FOM | 2021 | 0.41065 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
HighT-Molten-Salt | thermal | reference_value | FOM | 2021 | 4.4247 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
HighT-Molten-Salt | thermal | elec-salthight | FOM | 2021 | 2.2123 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 24
HighT-Molten-Salt | thermal | salthight-elec | FOM | 2021 | 2.2123 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 24
HighT-Molten-Salt | thermal | salthight-elec | efficiency | 2021 | 0.42424 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
HighT-Molten-Salt | thermal | elec-salthight | efficiency | 2021 | 0.99 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
HighT-Molten-Salt | thermal | salthight-elec | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
HighT-Molten-Salt | thermal | elec-salthight | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
HighT-Molten-Salt | thermal | salthight | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
LowT-Molten-Salt | thermal | saltlowt | investment | 2030 | 50.065 | $/kWh | Viswanathan_2022 | SB and BOS 0.85 of 2021 value | p.98 (p.120) | 1000 | 24
LowT-Molten-Salt | thermal | reference_value | investment | 2030 | 808.45 | $/kW | Viswanathan_2022 | Power Equipment 0.95 of 2021 value | p.98 (p.120) | 1000 | 24
LowT-Molten-Salt | thermal | elec-saltlowt | investment | 2030 | 161.69 | $/kW | Georgiou_2018 | Power Equipment Charge | Guesstimate that charge is 20% of capital costs of power components for sensible thermal storage
LowT-Molten-Salt | thermal | saltlowt-elec | investment | 2030 | 646.76 | $/kW | Georgiou_2018 | Power Equipment Discharge | Guesstimate that charge is 80% of capital costs of power components for sensible thermal storage
LowT-Molten-Salt | thermal |  | investment | 2030 | 15.0195 | $/kWh | Viswanathan_2022 | EPC fee Project Development Grid integration | p.98 (p.120) | 1000 | 24
LowT-Molten-Salt | thermal |  | FOM | 2030 | 0.21528 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
LowT-Molten-Salt | thermal | reference_value | FOM | 2030 | 3.4763 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
LowT-Molten-Salt | thermal | elec-saltlowt | FOM | 2030 | 1.7382 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 24
LowT-Molten-Salt | thermal | saltlowt-elec | FOM | 2030 | 1.7382 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 24
LowT-Molten-Salt | thermal | saltlowt-elec | efficiency | 2030 | 0.53939 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
LowT-Molten-Salt | thermal | elec-saltlowt | efficiency | 2030 | 0.99 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
LowT-Molten-Salt | thermal | saltlowt-elec | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
LowT-Molten-Salt | thermal | elec-saltlowt | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
LowT-Molten-Salt | thermal | saltlowt | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
LowT-Molten-Salt | thermal | saltlowt | investment | 2021 | 58.9 | $/kWh | Viswanathan_2022 | Molten Salt SB and BOS | p.101 (p.123) | 1000 | 24
LowT-Molten-Salt | thermal | reference_value | investment | 2021 | 834.6 | $/kW | Viswanathan_2022 | Power Equipment | p.101 (p.123) | 1000 | 24
LowT-Molten-Salt | thermal | elec-saltlowt | investment | 2021 | 166.92 | $/kW | Georgiou_2018 | Power Equipment Charge | Guesstimate that charge is 20% of capital costs of power components for sensible thermal storage
LowT-Molten-Salt | thermal | saltlowt-elec | investment | 2021 | 667.68 | $/kW | Georgiou_2018 | Power Equipment Discharge | Guesstimate that charge is 80% of capital costs of power components for sensible thermal storage
LowT-Molten-Salt | thermal |  | investment | 2021 | 17.67 | $/kWh | Viswanathan_2022 | EPC fee | p.101 (p.123) | 1000 | 24
LowT-Molten-Salt | thermal |  | FOM | 2021 | 0.25327 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
LowT-Molten-Salt | thermal | reference_value | FOM | 2021 | 3.5888 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
LowT-Molten-Salt | thermal | elec-saltlowt | FOM | 2021 | 1.7944 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 24
LowT-Molten-Salt | thermal | saltlowt-elec | FOM | 2021 | 1.7944 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 24
LowT-Molten-Salt | thermal | saltlowt-elec | efficiency | 2021 | 0.51919 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
LowT-Molten-Salt | thermal | elec-saltlowt | efficiency | 2021 | 0.99 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
LowT-Molten-Salt | thermal | saltlowt-elec | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
LowT-Molten-Salt | thermal | elec-saltlowt | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
LowT-Molten-Salt | thermal | saltlowt | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Concrete | thermal | concrete | investment | 2030 | 20.74 | $/kWh | Viswanathan_2022 | SB and BOS 0.85 of 2021 value | p.98 (p.120) | 1000 | 24
Concrete | thermal | reference_value | investment | 2030 | 808.45 | $/kW | Viswanathan_2022 | Power Equipment 0.95 of 2021 value | p.98 (p.120) | 1000 | 24
Concrete | thermal | elec-concrete | investment | 2030 | 161.69 | $/kW | Georgiou_2018 | Power Equipment Charge | Guesstimate that charge is 20% of capital costs of power components for sensible thermal storage
Concrete | thermal | concrete-elec | investment | 2030 | 646.76 | $/kW | Georgiou_2018 | Power Equipment Discharge | Guesstimate that charge is 80% of capital costs of power components for sensible thermal storage
Concrete | thermal |  | investment | 2030 | 6.222 | $/kWh | Viswanathan_2022 | EPC fee Project Development Grid integration | p.98 (p.120) | 1000 | 24
Concrete | thermal |  | FOM | 2030 | 0.089182 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
Concrete | thermal | reference_value | FOM | 2030 | 3.4763 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
Concrete | thermal | elec-concrete | FOM | 2030 | 1.7382 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 24
Concrete | thermal | concrete-elec | FOM | 2030 | 1.7382 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 24
Concrete | thermal | concrete-elec | efficiency | 2030 | 0.43434 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
Concrete | thermal | elec-concrete | efficiency | 2030 | 0.99 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
Concrete | thermal | concrete-elec | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Concrete | thermal | elec-concrete | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Concrete | thermal | concrete | lifetime | 2030 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Concrete | thermal | concrete | investment | 2021 | 24.4 | $/kWh | Viswanathan_2022 | SB and BOS | p.101 (p.123) | 1000 | 24
Concrete | thermal | reference_value | investment | 2021 | 1029.6 | $/kW | Viswanathan_2022 | Power Equipment | p.101 (p.123) | 1000 | 24
Concrete | thermal | elec-concrete | investment | 2021 | 205.92 | $/kW | Georgiou_2018 | Power Equipment Charge | Guesstimate that charge is 20% of capital costs of power components for sensible thermal storage
Concrete | thermal | concrete-elec | investment | 2021 | 823.68 | $/kW | Georgiou_2018 | Power Equipment Discharge | Guesstimate that charge is 80% of capital costs of power components for sensible thermal storage
Concrete | thermal |  | investment | 2021 | 8 | $/kWh | Viswanathan_2022 | EPC fee | p.101 (p.123) | 1000 | 24
Concrete | thermal |  | FOM | 2021 | 0.10492 | $/kWh-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
Concrete | thermal | reference_value | FOM | 2021 | 4.4273 | $/kW-year | Viswanathan_2022 | not provided calculated as for hydrogen | p 104 (p.126) | 1000 | 24
Concrete | thermal | elec-concrete | FOM | 2021 | 2.2136 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on charger |  | 1000 | 24
Concrete | thermal | concrete-elec | FOM | 2021 | 2.2136 | $/kW-year | Viswanathan_2022 | Guesstimate, 50% on discharger |  | 1000 | 24
Concrete | thermal | concrete-elec | efficiency | 2021 | 0.41414 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
Concrete | thermal | elec-concrete | efficiency | 2021 | 0.99 |  | Viswanathan_2022 | RTE assume 99% for charge and other for discharge | p.107 (p.129) | 1000 | 24
Concrete | thermal | concrete-elec | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Concrete | thermal | elec-concrete | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24
Concrete | thermal | concrete | lifetime | 2021 | 35 | years | Viswanathan_2022 |  | p.107 (p.129) | 1000 | 24